DM & MIXBED SOP

TO.

- Before system start, please clear raw water sufficient or not, If water sufficient, process for plant working.

- Before DM Plant start, Rinse to Cation & Anion Vessel with on/off raw water pump.

- After Rinse to DM Plant, MPV move to filter service for regular working.

- In Mixbed Plant, regular checking Conductivity/PH/Chloride etc.

- At  the time  of DM Plant Regeneration, please take NaoH & HCL (33%) as per mention in Technical Data Sheet.

- At the time DM Plant charge, first Regeneration to Cation & second Anion.

- In Mixbed Regeneration, first back wash to Vessel for separation Cation & Anion – 10 Min.

- Ensure, please check both resin separated or not, If separated – Start Regeneration process.

- In Regeneration, first Regeneration to Cation resin & second to Anion resin.

- Chemical use as per Technical Data Sheet.

- At the time of Regeneration, ensure NaoH Not use hot, It will be wait for cool.

- After Regeneration Cation & Anion resin, Plant to move rinse for 10 Min.

- After rinse, Air given to Mixbed plant, up to the both resin mix(5 to 10 Min)

- In system running, don’t move any MPV/ Valve.

- After Regeneration, please take Outlet Water Quality / Parameter/ Testing.

- Every day Maintain LOG Book / Record for Water Quality , Parameter

Design

- A-Online PH meter

- B-Online Conductivity Meter

- C-Online Rota meter

Cation

Anion

B

A

Outlet water

Mix bed  plant

Mix bed Plant

C

RWP

- Cation Resin 450 Ltr

- Anion Resin 450 ltr

- Mixbed Resin 1) Cation 150  Ltr

2) Anion 270 Ltr

RO PLANT SOP